SMART TUNNEL IoT SYSTEM

User, Installation, Blynk Configuration & Operation Manual

ESP32 + MQ2 + BH1750 + L298N + DC Fan + Blynk
Automatic Air-Quality-Based Ventilation Control

Document purpose: provide a complete, reproducible procedure for building, configuring, programming, testing, and operating the current MQ2-based Smart Tunnel prototype.

# 1. Project Overview

The Smart Tunnel prototype uses an ESP32 as the main controller. An MQ2 analog sensor provides a raw air-quality/gas sensor reading, a BH1750 measures illumination in lux, and an L298N motor driver controls a DC fan. Blynk provides cloud connectivity and a dashboard for monitoring and manual/automatic fan control.

The automatic ventilation function evaluates the MQ2 raw ADC value and selects one of four fan states: OFF, LOW, MEDIUM, or HIGH. The threshold values supplied in this manual are starting values and must be calibrated experimentally for the actual sensor and tunnel.

## 1.1 Current implementation scope

| Function | Status |
| --- | --- |
| ESP32 controller | Implemented |
| MQ2 analog air-quality reading | Implemented |
| BH1750 light measurement | Implemented |
| Automatic fan control | Implemented |
| Manual fan control through Blynk | Implemented |
| Blynk cloud monitoring | Implemented |
| Pollution event notification | Implemented |
| Low-light event notification | Implemented |
| ESP32-CAM/video surveillance | Not implemented in this firmware |
| MQ135 sensor | Not used by this firmware; code uses MQ2 |

## 1.2 Important consistency note

The supplied firmware uses MQ2 on GPIO 34. If the project paper states MQ135, either replace the physical sensor and firmware accordingly or revise the paper to accurately describe MQ2. Do not claim MQ135 operation while using the MQ2 firmware.

# 2. Required Hardware

| Item | Quantity | Purpose |
| --- | --- | --- |
| ESP32 development board | 1 | Main controller and Wi-Fi |
| MQ2 sensor/module | 1 | Raw analog gas/air-quality signal |
| BH1750 | 1 | Ambient light measurement |
| L298N motor driver | 1 | Interfaces ESP32 with DC fan |
| DC fan | 1 | Tunnel ventilation |
| External motor power supply | 1 | Powers fan/L298N motor side |
| Jumper wires | As needed | Connections |
| Breadboard/prototype wiring | 1 | Assembly |
| USB cable | 1 | Programming ESP32 |

## 2.1 Power and safety notes

Never power a larger DC fan directly from an ESP32 GPIO. Use the L298N and an appropriate external motor supply. ESP32 GND and L298N GND must share a common ground.

Before connecting the MQ2 analog output to GPIO 34, verify the module's analog-output voltage. ESP32 GPIOs are 3.3 V logic. If the sensor/module can output above 3.3 V, use an appropriate voltage divider/level-shifting arrangement or a safe sensor configuration.

# 3. Software Requirements

| Software | Purpose |
| --- | --- |
| Arduino IDE | Compile and upload ESP32 firmware |
| ESP32 Arduino board package | ESP32 support in Arduino IDE |
| Blynk library | Blynk.Cloud communication |
| BH1750 library | BH1750 light sensor interface |
| Blynk account | Cloud dashboard, device, datastreams and events |

## 3.1 Install Arduino IDE

Install Arduino IDE from the official Arduino website. Then open Arduino IDE.

## 3.2 Install ESP32 board support

Open File > Preferences > Additional Boards Manager URLs and add:

https://raw.githubusercontent.com/espressif/arduino-esp32/gh-pages/package_esp32_index.json

Then open Tools > Board > Boards Manager, search for “esp32”, and install “esp32 by Espressif Systems”. Select ESP32 Dev Module unless your board requires another exact model.

## 3.3 Install libraries

Open Sketch > Include Library > Manage Libraries and install:

• Blynk
• BH1750

# 4. Blynk Cloud Configuration

Blynk uses Device Templates to define common configuration, datastreams, events and dashboards. A device inherits its template configuration. Datastreams are channels through which values move between the hardware and Blynk.Cloud; widgets can display values and can also send values back to the device.

Official Blynk documentation: https://docs.blynk.io/en/concepts/device-template

Official Datastream documentation: https://docs.blynk.io/en/blynk.console/templates/datastreams

## 4.1 Enable Developer Mode

Log in to Blynk.Console and make sure Developer Mode is enabled. The exact menu wording may vary slightly with the current Blynk interface.

## 4.2 Create the template

Create a new Device Template with:

| Setting | Recommended value |
| --- | --- |
| Template Name | Smart Tunnel |
| Hardware | ESP32 |
| Connection | WiFi |

## 4.3 Obtain BLYNK_TEMPLATE_ID

Open the Smart Tunnel template and copy its Template ID. It normally looks like TMPLxxxxxxxx. Paste it into the firmware:

#define BLYNK_TEMPLATE_ID "TMPLxxxxxxxx"

## 4.4 Set BLYNK_TEMPLATE_NAME

#define BLYNK_TEMPLATE_NAME "Smart Tunnel"

Use the same name as the template you created.

## 4.5 Create the device and obtain BLYNK_AUTH_TOKEN

Go to Devices, create a new device from the Smart Tunnel template, and open the device information/developer tools area to obtain its AuthToken. Blynk states that each device has a unique AuthToken used to authenticate the device with Blynk.Cloud.

Official activation guide: https://docs.blynk.io/en/getting-started/activating-devices/manual-device-activation

#define BLYNK_AUTH_TOKEN "YOUR_BLYNK_AUTH_TOKEN"

## 4.6 Configure Wi-Fi

char ssid[] = "YOUR_WIFI_NAME";
char pass[] = "YOUR_WIFI_PASSWORD";

Replace these placeholders with the Wi-Fi network used by the ESP32. For typical ESP32 deployments, use a compatible 2.4 GHz Wi-Fi network.

# 5. Blynk Datastream Configuration

Create five Virtual Pin datastreams in the Smart Tunnel template. The firmware uses V0 through V4.

| Pin | Name | Type | Range | Direction/Purpose |
| --- | --- | --- | --- | --- |
| V0 | Air Quality | Integer | 0–4095 | ESP32 → Blynk; MQ2 raw ADC |
| V1 | Fan Mode | Integer | 0–1 | Blynk → ESP32; 0 Manual, 1 Automatic |
| V2 | Light | Double | 0–10000+ | ESP32 → Blynk; lux |
| V3 | Fan Speed | Integer | 0–255 | ESP32 → Blynk; current PWM |
| V4 | Manual Fan Speed | Integer | 0–255 | Blynk → ESP32; manual PWM |

## 5.1 V0 — Air Quality

Create a Virtual Pin datastream:

| Setting | Value |
| --- | --- |
| Name | Air Quality |
| Pin | V0 |
| Type | Integer |
| Min | 0 |
| Max | 4095 |

## 5.2 V1 — Fan Mode

| Setting | Value |
| --- | --- |
| Name | Fan Mode |
| Pin | V1 |
| Type | Integer |
| Min | 0 |
| Max | 1 |

0 = Manual mode; 1 = Automatic mode.

## 5.3 V2 — Light

| Setting | Value |
| --- | --- |
| Name | Light |
| Pin | V2 |
| Type | Double |
| Unit | Lux |
| Recommended range | 0–10000 |

## 5.4 V3 — Fan Speed

| Setting | Value |
| --- | --- |
| Name | Fan Speed |
| Pin | V3 |
| Type | Integer |
| Min | 0 |
| Max | 255 |

## 5.5 V4 — Manual Fan Speed

| Setting | Value |
| --- | --- |
| Name | Manual Fan Speed |
| Pin | V4 |
| Type | Integer |
| Min | 0 |
| Max | 255 |

# 6. Blynk Events and Notifications

Create these events in the template. Event codes must exactly match the strings used in Blynk.logEvent().

| Event name | Event code | Trigger |
| --- | --- | --- |
| Pollution Alert | pollution_alert | MQ2 reading above clean threshold |
| Low Light Alert | lightdamage | BH1750 reading below light threshold |

Enable notifications for these events if you want mobile alerts. The firmware uses a cooldown so repeated alerts are not generated every second.

# 7. Dashboard Configuration

| Widget | Datastream | Recommended display |
| --- | --- | --- |
| Gauge/Value | V0 | Air Quality |
| Switch | V1 | Automatic/Manual |
| Gauge/Value | V2 | Tunnel Light (lux) |
| Gauge/Value | V3 | Fan Speed (0–255) |
| Slider | V4 | Manual Fan Speed (0–255) |

Recommended dashboard logic:

• V1 ON = Automatic fan control.
• V1 OFF = Manual fan control.
• V4 changes fan speed only in Manual mode.
• V3 shows the actual current PWM value.

# 8. Hardware Wiring

| Component | Pin/Terminal | ESP32/Power connection |
| --- | --- | --- |
| MQ2 | AO | GPIO 34 |
| MQ2 | GND | ESP32 GND |
| MQ2 | VCC | Use a safe supply/configuration; verify AO voltage |
| BH1750 | SDA | GPIO 21 |
| BH1750 | SCL | GPIO 22 |
| BH1750 | GND | GND |
| BH1750 | VCC | 3.3 V recommended for ESP32 I2C setup |
| L298N | ENA | GPIO 15 (PWM) |
| L298N | IN1 | GPIO 2 |
| L298N | IN2 | Optional; firmware leaves it unused (-1) |
| L298N | GND | Common GND with ESP32 |
| L298N | OUT1/OUT2 | DC fan |
| L298N | Motor supply | External supply appropriate for fan |

The firmware uses Wire.begin(21, 22) in the reference implementation below, making the I2C pin assignment explicit.

# 9. Automatic Fan Control

The current starting thresholds are:

| MQ2 raw ADC | Condition | Fan PWM | Fan state |
| --- | --- | --- | --- |
| 0–490 | Clean | 0 | OFF |
| 491–900 | Moderate | 90 | LOW |
| 901–1500 | Poor | 170 | MEDIUM |
| >1500 | Very poor | 255 | HIGH |

These are raw ADC thresholds, not ppm values and not a validated air-quality index. MQ sensors require warm-up and application-specific calibration. For research reporting, document how thresholds were selected and do not label them as standardized gas concentration limits unless you have performed the required calibration.

# 10. Compile and Upload

1. Connect the ESP32 to the computer with USB.

2. Select Tools > Board > ESP32 Arduino > ESP32 Dev Module (or your exact board).

3. Select Tools > Port and choose the ESP32 COM port.

4. Paste the completed firmware into Arduino IDE.

5. Compile/Verify the sketch.

6. Upload the sketch.

7. If the board remains at Connecting during upload, press/hold BOOT as required by your board until upload begins.

8. Open Tools > Serial Monitor and set 115200 baud.

# 11. Expected Serial Monitor Output

=================================
 Smart Tunnel Monitoring System
=================================
BH1750 initialized successfully.
Connecting to Blynk...
Blynk connected.
Fan PWM: 0
System started.

Air Quality Sensor: 420
Fan PWM: 0
Light: 1350.25 lx
--------------------------------
Air Quality Sensor: 720
Fan PWM: 90
Light: 1100.40 lx
--------------------------------

# 12. Operating Procedure

## 12.1 Automatic mode

Turn V1 ON. The ESP32 reads the MQ2 every second. The automatic control routine maps the raw reading to a fan speed. The fan speed is changed only when the selected speed differs from the current speed.

## 12.2 Manual mode

Turn V1 OFF. Adjust V4 from 0 to 255. The fan follows the manual PWM value. V3 reports the resulting current fan speed.

## 12.3 Light monitoring

BH1750 readings are sent to V2. If the reading is below 1000 lux, the low-light event can be generated, subject to the 60-second event cooldown.

# 13. Commissioning and Test Plan

| Test | Procedure | Expected result |
| --- | --- | --- |
| Wi-Fi | Power ESP32 and inspect Serial Monitor | Blynk connects |
| MQ2 | Observe raw readings after warm-up | V0 changes with sensor conditions |
| Automatic fan | Increase MQ2 reading in a controlled test | Fan changes OFF→LOW→MEDIUM→HIGH |
| Manual fan | Set V1=0 and move V4 | Fan follows manual PWM |
| BH1750 | Cover/expose sensor | V2 changes in lux |
| Low-light alert | Reduce light below threshold | lightdamage event after cooldown |
| Pollution alert | Raise MQ2 reading above threshold | pollution_alert event after cooldown |
| Blynk dashboard | Observe all widgets | Values update correctly |

# 14. MQ2 Calibration and Threshold Tuning

Do not finalize the 490/900/1500 thresholds solely because they work in a demonstration. First record baseline readings under normal tunnel conditions. Repeat measurements under several controlled conditions and choose thresholds from the observed distribution and the application's ventilation requirements.

Recommended data table for experiments:

| Test condition | MQ2 raw reading | Fan PWM | Response time | Notes |
| --- | --- | --- | --- | --- |
| Normal air |  |  |  |  |
| Moderate test condition |  |  |  |  |
| High test condition |  |  |  |  |
| Very high test condition |  |  |  |  |

If you need actual ppm or a standardized air-quality metric, use a sensor and calibration method appropriate to the gas being measured. A raw MQ2 ADC value should not be reported as a ppm measurement.

# 15. Troubleshooting

| Problem | Likely cause | Action |
| --- | --- | --- |
| Blynk never connects | Wrong Template ID/AuthToken/Wi-Fi | Recheck credentials and device/template association |
| Dashboard shows no V0 | Missing/wrong V0 datastream | Create V0 as Integer and verify widget assignment |
| Fan does not rotate | Power/wiring/L298N issue | Check external supply, common GND, ENA and motor output |
| Fan speed does not change | ENA/PWM wiring or jumper issue | Connect GPIO 15 to ENA and configure the driver for PWM |
| MQ2 stays at 0 | Wrong pin/power/AO connection | Check AO→GPIO34 and sensor supply |
| BH1750 fails | SDA/SCL/power/wiring | Check SDA=21, SCL=22 and I2C supply |
| Events do not trigger | Event code mismatch | Make Blynk event code exactly match firmware string |
| Upload stuck at Connecting | Board bootloader timing | Hold BOOT during upload if required |
| False pollution alerts | MQ2 warm-up/calibration | Warm up sensor and recalibrate thresholds |

# 16. Security and GitHub Publishing

Never publish a real Wi-Fi password or Blynk AuthToken in a public repository. Blynk documents AuthToken as the unique identifier used to authenticate a device and recommends not exposing it publicly.

#define BLYNK_AUTH_TOKEN "YOUR_BLYNK_AUTH_TOKEN"
char ssid[] = "YOUR_WIFI_NAME";
char pass[] = "YOUR_WIFI_PASSWORD";

For a public GitHub project, keep credentials in a private/local configuration mechanism or inject them during deployment. If a real token or password has already been exposed, rotate/revoke it.

# 17. Final Deployment Checklist

☐ Template ID entered correctly

☐ Template name matches Blynk template

☐ AuthToken entered and kept private

☐ Wi-Fi SSID and password entered

☐ V0–V4 datastreams created

☐ pollution_alert event created

☐ lightdamage event created

☐ Dashboard widgets assigned to correct datastreams

☐ MQ2 AO connected to GPIO 34 safely

☐ BH1750 SDA/SCL connected to GPIO 21/22

☐ L298N ENA connected to GPIO 15

☐ L298N IN1 connected to GPIO 2

☐ ESP32 and L298N share GND

☐ Fan has an appropriate external power supply

☐ MQ2 warmed up and thresholds calibrated

☐ Automatic mode tested

☐ Manual mode tested

☐ Blynk notifications tested

☐ No credentials committed to public GitHub